Interworking

KNX Association

Table of Contents

1	Introduction	5

2	Advantages of Interworking	5

3	Principles of KNX Interworking	6

3.1	Introduction	6

3.2	Coding of Datapoint types	7

3.2.1	Introduction	7

3.2.2	Principle Datapoint types classes	7

3.2.3	Structured Types	8

3.2.4	“Multi-state” Types	8

3.2.5	Status Types	10

4	KNX common datapoint types	11

4.1	Introduction	11

4.2	Boolean Data	11

4.2.1	General	11

4.2.2	Datapoint types B1	11

4.3	1 Bit with priority control	13

4.3.1	General	13

4.3.2	Datapoint types B2	14

4.4	3 Bit with Control	15

4.4.1	General	15

4.4.2	Datapoint DPT_Control_Dimming	15

4.4.3	Datapoint DPT_Control_Blinds	16

4.5	Character Set	17

4.5.1	General	17

4.5.2	Datapoint types Character Set	17

4.6	8 Bit without Sign	18

4.6.1	General	18

4.6.2	Scaled values	18

4.6.3	Non-Scaled values	19

4.7	8 Bit with Sign	19

4.7.1	General	19

4.7.2	Datapoint types V8 - Signed Relative Value	19

4.8	2 Octet without Sign	20

4.8.1	General	20

4.8.2	2-octet unsigned counter value	20

4.9	2 Octet with Sign	21

4.9.1	General	21

4.9.2	2-octet signed counter value	21

4.10	2 Octet Floating Point Number	22

4.10.1	General	22

4.10.2	Datapoint types 2-Octet Float Value	23

4.10.3	Example	23

4.11	Time	25

4.11.1	General	25

4.11.2	Datapoint type Time	25

4.12	Date	26

4.12.1	General	26

4.12.2	Datapoint type Date	26

4.13	Date and Time	26

4.13.1	Datapoint type Time and Date	27

4.13.2	Comments	28

4.14	4 Octet without Sign	30

4.14.1	General	30

4.14.2	Datapoint typeDatapoint types 4-Octet Unsigned Value	30

4.15	4 Octet with Sign	30

4.15.1	General	30

4.15.2	Datapoint type 4-Octet Signed Value	30

4.16	4 Octet Floating Point Number	31

4.16.1	General	31

4.16.2	Datapoint types 4-Octet Float Value	31

4.17	Access Control	32

4.17.1	General	32

4.17.2	Datapoint type DPT_Access_Data	32

4.18	Character String	33

4.18.1	General	33

4.18.2	Example	33

4.19	Scene Control	33

4.19.1	General	33

4.19.2	Datapoint type Scene Number	33

4.19.3	Datapoint type DPT_SceneControl	34

4.20	Common HVAC Datapoint types	34

4.20.1	General	34

4.21	Datapoint types N8	34

5	Combination of DPTs into devices	36

5.1	General	36

5.2	Functional Block – Dimming Actuator Basic	36

5.2.1	General	36

5.2.2	Dimming Actuator Basic – Status Diagram	37

5.3	Functional Block – Sunblind Actuator Basic	38

5.3.1	General	38

5.3.2	Sunblind Actuator Basic – Status Diagram	39

# Introduction

Already under the predecessor system to KNX, i.e. EIB, the Association not only took care of the standardisation of the protocol but also laid down rules for the encoding of the useful data inside telegrams.

Without standardisation of this aspect, devices of different manufacturers would be able to talk KNX but could still code the useful data contained in the tail of the telegram differently, e.g. manufacturer A would code temperatures as 1 byte and another as 3 bytes.

For a start such group objects could then not be linked by means of ETS and secondly, these devices would not understand one another.

In order to ensure interworking between manufacturers and even products of different application domains, KNX Association therefore laid down formats for common functions like switching, dimming, blinds control, integer and float values, percentage, date/time, HVAC modes, scene control, …. These formatsare referred to as “KNX standardized Data types”.

The most common data types were also standardized on a European level and integrated into the EN 50090 series as Part 3-3.

If a standardized format for a certain function exists, for certification the KNX manufacturer is obliged to use this format. Compliance to the format is also checked during the KNX interworking tests as carried out by KNX accredited test labs.

# Advantages of Interworking

The benefits of Home and Building Control only become truly visible when devices of different manufacturers and different application domains interwork:

Presence detector is part of the alarm system at night;

Room thermostat of Manufacturer A sets position of valves of Manufacturer B;

“All off” button of Manufacturer A switches the lights off, controlled by switching actuators of Manufacturer B, C, D, …;

Scheduler of Manufacturer A ensures presence simulation, thereby controlling blinds of Manufacturer B

It goes without saying that this is an enormous benefit to end users. When a product line A is defective but Manufacturer A has discontinued product line, the end user can find a replacement at Manufacturer B.

A system with true interworking also attracts manufacturers of niche products, as one single manufacturer can simply not offer all possible HBES solutions, from lighting to HVAC to Load management, etc.

This in turn boosts the OEM market: what Manufacturer A does not produce himself, he can easily find at another HBES manufacturer and complete his offer by relabeling the products he buys from Manufacturer A.

Gateway solutions between KNX and proprietary or other standardized systems (e.g. DALI, BACnet, …) are easier to develop, as the proprietary encoding can be easily mapped to common KNX data formats as described in the KNX standard.

Last but not least, it would have been impossible for KNX to establish the common market infrastructure that exists today:

the fact that all products of all manufacturers can be linked to one working installation is the corner stone of the KNX one configuration tool (ETS) approach.

It would have been impossible to establish the common training scheme for the training of persons interested in using the KNX technology in home or commercial projects. The training scheme of Basic, Advanced and Tutor courses is worldwide standardized. In contrast to that, manufacturers of proprietary systems must establish each individually their own training schemes and users of such material must visit several courses if they wish to combine material of several manufacturers into an installation.

# Principles of KNX Interworking

## Introduction

For KNX devices that are programmed with the ETS, KNX requires that at least the group objects are coded according to KNX standardized data types. The encoding of parameters that are described in the product data  descriptions can be manufacturer specific.

For some of the device types (e.g. like dimming, blind control or switching with priority), it is however necessary that actuators show a certain behaviour when data is sent to the available group objects. In this case, the specification of functional blocks becomes necessary and needs to be complied with during KNX product certification.

Functional blocks group a number of inputs, outputs and parameters. For this combination, a precise function description is provided.

| Inputs |  | Function block Name |  |  |  | Outputs |
| --- | --- | --- | --- | --- | --- | --- |
|  | DPT I1 |  |  |  | DPT O1 |  |
| Description I1 | --------- | I1 |  | O1 | --------- | Description O1 |
|  | DPT I2 |  |  |  |  |  |
| Description I2 | --------- | I2 |  |  |  |  |
| Parameters |  |  |  |  |  |  |
|  | DPT P1 |  |  |  |  |  |
|  | --------- | P1 |  |  |  |  |

Especially when devices support Easy installation, a clear definition of the description of each channel in the device in the form of functional blocks is necessary.

## Coding of Datapoint types

### Introduction

A group object is regarded as a certain type of datapoint. Also parameters can be regarded as datapoints.

The Datapoint type is determined by the following four elements

- Format:	Which fields is the Datapoint type composed of? Each field can consist of one or several bits.

- Coding:	How is the data encoded?

- Value range:	Are there any limitations to the value range? There may be different minimum and maximum values or valid values for each field or lists of valid values.

- Unit:	Which units does the data of the individual fields have?

### Principle Datapoint types classes

#### Introduction

Five classes can be distinguished according to their internal structure. More explanation is given in the next clauses.

#### Simple Types

Examples of simple types are: boolean values, pure numerical values.

#### Enumerated Types

Enumerations are used for datapoints with a clearly limited number of values and no precise hierarchical order. If a datapoint uses an enumerated data type, all possible states shall be described. If invalid / undefined values are sent, no malfunctions may occur.

Examples are: Toggling between “Comfort”, “Standby” “Night”,… operating modes in room thermostats.

### Structured Types

Structured Datapoint types consist of several parts which are combined in a datapoint. Only fields which cannot be interpreted meaningfully on their own can be combined to a structured Datapoint type.

Examples are : KNX relative dimming (3.007 DPT_Control_Dimming)

### “Multi-state” Types

Multi-state Datapoint types are intended for transmitting data

of which the encodable values follow a hierarchical sequence and

of which all encodable values are meaningful

Examples: a fan controller (motor) can drive the fan from standstill over 5 positions up to a maximum speed.

#### Definition

To be able to cover all cases in which senders and receivers operate with many different steps, they both convert their steps to a range between 0 and 255.

The following applies for the sender:

This value is rounded up or down and sent as a byte without a sign.

The following applies for the receiver:

Example: A sender with 3 steps (NS=3) controls a receiver with 5 steps (NR=5).
Step 2 (S x=2) of the sender is thus transmitted as = 170. The receiver interprets this as and moves to its level 3.

These Datapoint types can only be used if

the states have a clearly defined sequence,

no exact linear conversion of the steps between sender and receiver is required

### Status Types

Datapoint types for transmitting status information should meet two goals:

- A device should be able to report its operating mode to other devices.

- A device should be able to be switched to a specific operating mode.

To achieve this, further bits are sent as a mask in addition to the actual status information. The mask determines whether the data of the status fields should be used as valid commands or only for information purposes.

These Datapoint types are primarily used in the area of heating technology.

# KNX common datapoint types

## Introduction

This section lists some common KNX Datapoint types.

All Datapoint types have a unique identification consisting of two digits. The first digit denotes the format and the encoding. The second digit represents the value range and the unit.

In the course of technical development, KNX members may submit suggestions for new Datapoint types to the KNX Association. New Datapoint types are also drawn up by the responsible KNX working group ‘WGI’ (Working Group Interworking) when elaborating new application descriptions and corresponding KNX standardised functional blocks.

Group objects complying to DPT types with a size of 6 bits or less only use the bits directly following the APCI (any unused bits are set to zero) in the KNX telegram. Any group objects complying to DPTs with a size greater than 6 bits will result in telegrams, where the 6 bits following the APCI are set to zero and the useful data padded after these unused bits.

## Boolean Data

### General

DPT ID 1.xxx is used for all possible applications in which two different values are to be set or sent.

### Datapoint types B1

| Format: |  | 1 bit: B1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| octet nr |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| field names |  |  |  |  |  |  |  |  |  | b |  |  |  |  |  |  |  |  |
| encoding |  |  |  |  |  |  |  |  |  | B |  |  |  |  |  |  |  |  |
| Range: |  | b = {0,1} |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Unit: |  | None. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Resol.: |  | (not applicable) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Datapoint types |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ID: | Name: |  |  |  |  |  |  |  |  |  |  |  | Encoding: b |  |  |  |  |  |
| 1.001 | DPT_Switch |  |  |  |  |  |  |  |  |  |  |  | 0 = Off 1 = On |  |  |  |  |  |
| 1.002 | DPT_Bool |  |  |  |  |  |  |  |  |  |  |  | 0 = False 1 = True |  |  |  |  |  |
| 1.003 | DPT_Enable |  |  |  |  |  |  |  |  |  |  |  | 0 = Disable 1 = Enable |  |  |  |  |  |
| 1.004 | DPT_Ramp |  |  |  |  |  |  |  |  |  |  |  | 0 = No ramp 1 = Ramp |  |  |  |  |  |
| 1.005 | DPT_Alarm |  |  |  |  |  |  |  |  |  |  |  | 0 = No alarm 1 = Alarm |  |  |  |  |  |
| 1.006 | DPT_BinaryValue |  |  |  |  |  |  |  |  |  |  |  | 0 = Low 1 = High |  |  |  |  |  |
| 1.007 | DPT_Step |  |  |  |  |  |  |  |  |  |  |  | 0 = Decrease 1 = Increase |  |  |  |  |  |
| 1.008 | DPT_UpDown |  |  |  |  |  |  |  |  |  |  |  | 0 = Up 1 = Down |  |  |  |  |  |
| 1.009 | DPT_OpenClose |  |  |  |  |  |  |  |  |  |  |  | 0 = Open 1 = Close |  |  |  |  |  |
| 1.010 | DPT_Start |  |  |  |  |  |  |  |  |  |  |  | 0 = Stop 1 = Start |  |  |  |  |  |
| 1.011 | DPT_State |  |  |  |  |  |  |  |  |  |  |  | 0 = Inactive 1 = Active |  |  |  |  |  |
| 1.012 | DPT_Invert |  |  |  |  |  |  |  |  |  |  |  | 0 = Not inverted 1 = Inverted |  |  |  |  |  |
| 1.013 | DPT_DimSendStyle |  |  |  |  |  |  |  |  |  |  |  | 0 = Start/stop 1 = Cyclically |  |  |  |  |  |
| 1.014 | DPT_InputSource |  |  |  |  |  |  |  |  |  |  |  | 0 = Fixed 1 = Calculated |  |  |  |  |  |
| 1.015 | DPT_Reset |  |  |  |  |  |  |  |  |  |  |  | 0 = no action (dummy) 1 = reset command (trigger) |  |  |  |  |  |
| 1.016 | DPT_Ack |  |  |  |  |  |  |  |  |  |  |  | 0 = no action (dummy) 1 = acknowledge command (trigger), e.g. for alarming |  |  |  |  |  |
| 1.017 | DPT_Trigger |  |  |  |  |  |  |  |  |  |  |  | 0, 1 = trigger |  |  |  |  |  |
| 1.018 | DPT_Occupancy |  |  |  |  |  |  |  |  |  |  |  | 0 = not occupied 1 = occupied |  |  |  |  |  |
| 1.019 | DPT_Window_Door |  |  |  |  |  |  |  |  |  |  |  | 0 = closed 1 = open |  |  |  |  |  |
| 1.021 | DPT_LogicalFunction |  |  |  |  |  |  |  |  |  |  |  | 0 = logical function OR 1 = logical function AND |  |  |  |  |  |
| 1.022 | DPT_Scene_AB |  |  |  |  |  |  |  |  |  |  |  | 0 = scene A 1 = scene B |  |  |  |  |  |
| 1.023 | DPT_ShutterBlinds_Mode |  |  |  |  |  |  |  |  |  |  |  | 0 = only move Up/Down mode (shutter) 1 = move Up/Down + StepStop mode (blind) |  |  |  |  |  |

## 1 Bit with priority control

### General

These Datapoint types are intended for applications offering a priority control that has precedence over the normal (manual) operation. In other words, if an actuator is switched via its priority datapoint, switching via its usual DPT 1.xxx group objects is disabled.

Switching with priority is ensured via 2-bit Datapoint types.

The interaction between the 2 and the 1 bit datapoint functions according to the underneath diagram.

### Datapoint types B2

| Format: | 2 bit: B2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| octet nr |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| field names |  |  |  |  |  |  |  | c | V |  |  |  |  |  |  |  |  |  |  |  |  |  |
| encoding |  |  |  |  |  |  |  | B | B |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Range: | c = {0,1} v = {0,1} |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Unit: | None |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Resol.: | (not applicable) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Datapoint types |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ID: | Name: |  |  |  |  |  |  |  |  |  |  | Encoding: |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | c |  |  |  |  |  |  |  | v |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | 0 = no control 1 = control |  |  |  |  |  |  |  | According to Type 1.xxx |  |  |
| 2.001 | DPT_Switch_Control |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2.002 | DPT_Bool_Control |  |  |  |  |  |  |  |  |  |  |  |  |  | c | v |  |  |  |  |  |  |
| 2.003 | DPT_Enable_Control |  |  |  |  |  |  |  |  |  |  |  |  |  | 0 | 0 |  | No control |  |  |  |  |
| 2.004 | DPT_Ramp_Control |  |  |  |  |  |  |  |  |  |  |  |  |  | 0 | 1 |  | No control |  |  |  |  |
| 2.005 | DPT_Alarm_Control |  |  |  |  |  |  |  |  |  |  |  |  |  | 1 | 0 |  | Control. Function value 0 |  |  |  |  |
| 2.006 | DPT_BinaryValue_Control |  |  |  |  |  |  |  |  |  |  |  |  |  | 1 | 1 |  | Control. Function value 1 |  |  |  |  |
| 2.007 | DPT_Step_Control |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2.008 | DPT_Direction1_Control |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2.009 | DPT_Direction2_Control |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2.010 | DPT_Start_Control |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2.011 | DPT_State_Control |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2.012 | DPT_Invert_Control |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

## 3 Bit with Control

### General

These Datapoint types are amongst others used to realize relative dimming or moving blinds relative to a certain start position.

### Datapoint DPT_Control_Dimming

| Format: | 4 bit: B1U3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| octet nr |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| field names |  |  |  |  |  | c | StepCode |  |  |  |  |  |  |  |  |  |
| encoding |  |  |  |  |  | B | U | U | U |  |  |  |  |  |  |  |
| Range: | c = {0,1} StepCode = [000b…111b] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Unit: | None |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Resol.: | (not applicable) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Datapoint types |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ID: | Name: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.007 | DPT_Control_Dimming |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| Data fields | Description | Encoding |
| --- | --- | --- |
| c | Increase or decrease the brightness. | See 1.007 0 = Decrease 1 = Increase |
| StepCode | The amount of intervals into which the range of 0 % … 100 % is subdivided, or the break indication. | - 001b…111b: Step Number of intervals = 2^(stepcode-1) - 000b: Break |

### Datapoint DPT_Control_Blinds

| Format: | 4 bit: B1U3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| octet nr |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| field names |  |  |  |  |  | c | StepCode |  |  |  |  |  |  |  |  |  |
| encoding |  |  |  |  |  | B | U | U | U |  |  |  |  |  |  |  |
| Range: | c = {0,1} StepCode = [000b…111b] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Unit: | none |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Resol.: | (not applicable) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Datapoint types |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ID: | Name: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.008 | DPT_Control_Blinds |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| Data fields | Description | Encoding |
| --- | --- | --- |
| c | Move up or down. | See 1.008 0 = Up 1 = Down |
| StepCode | The amount of intervals into which the range of 0 % … 100 % is subdivided, or the break indication. | - 001b…111b: Step Number of intervals = 2^(stepcode-1) - 000b: Break |

- This DPT can be used both for the relative positioning of the vertical blinds positions as well as for the relative positioning of the angle of the slats.

## Character Set

### General

DPT 4.xxx is defined for transmitting individual (text) characters. The encoding sent on the bus corresponds to the coordinates of a look up table, containing the different characters.

### Datapoint types Character Set

| Format |  | 8 bit |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  | 1 |  |  |  |
|  |  | AAAAAAAA |  |  |  |
| Encoding |  | See below |  |  |  |
| Range |  | See below |  |  |  |
| Unit |  | - |  |  |  |
| Datapoint types |  |  |  |  |  |
| ID: | Name: |  |  | Range: | Encoding: |
| 4.001 | DPT_Char_ASCII |  |  | [0…127] | See below. The most significant bit shall always be 0 |
| 4.002 | DPT_Char_8859_1 |  |  | [0…255] | See below |
| Encoding: |  |  |  |  |  |
| 4.001 | DPT_Char_ASCII |  |  | AAAA; AAAA; LSN = Least Significant Nibble. MSN; LSN; MSN = Most Significant Nibble. MSN; 0; 1; 2; 3; 4; 5; 6; 7; 8; 9; A; B; C; D; E; F. LSN. 0; NUL; DLE; 0; @; P; `; p; °; À; Ð; à; ð. 1; SOH; DC1; !; 1; A; Q; a; q; ¡; ±; Á; Ñ; á; ñ. 2; STX; DC2; “; 2; B; R; b; r; ¢; ²; Â; Ò; â; ò. 3; ETX; DC3; #; 3; C; S; c; s; £; ³; Ã; Ó; ã; ó. 4; EOT; DC4; $; 4; D; T; d; t; ¤; ´; Ä; Ô; ä; ô. 5; ENQ; NAK; %; 5; E; U; e; u; ¥; µ; Å; Õ; å; õ. 6; ACK; SYN; &; 6; F; V; f; v; ¦¯; ¶; Æ; Ö; æ; ö. 7; BEL; ETB; ‘; 7; G; W; g; w; §; ·; Ç; ×; ç; ÷. 8; BS; CAN; (; 8; H; X; h; x; ¨; ¸; È; Ø; è; ø. 9; HT; EM; ); 9; I; Y; i; y; ©; ¹; É; Ù; é; ù. A; LF; SUB; *; :; J; Z; j; z; ª; º; Ê; Ú; ê; ú. B; VT; ESC; +; ;; K; [; k; {; «; »; Ë; Û; ë; û. C; FF; FS; ,; <; L; \; l; ¦; ¬; ¼; Ì; Ü; ì; ü. D; CR; GS; -; =; M; ]; m; }; ­; ½; Í; Ý; í; ý. E; SO; RS; .; >; N; ^; n; ~; ®; ¾; Î; Þ; î; þ. F; SI; US; /; ?; O; o; ¯; ¿; Ï; ß; ï; ÿ. |
| 4.002 | DPT_Char_8859_1 |  |  |  |  |

## 8 Bit without Sign

### General

DPT 5.xxx is defined for transmitting unsigned values up to 255.

### Scaled values

| Format: |  | 8 bit: U8 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| octet nr |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| field names |  |  | Unsigned Value |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Encoding |  |  | U | U | U | U | U | U | U | U |  |  |  |  |  |  |  |  |  |  |
| Encoding: |  | binary encoded msb lsb. U; U; U; U; U; U; U; U. 0; 0; 0; 0; 0; 0; 0; 0; = range min. /off. 0; 0; 0; 0; 0; 0; 0; 1; = value “low”. 1; 1; 1; 1; 1; 1; 1; 1; = range max.. |
| Range: |  | U = [0…255] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Datapoint types |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ID: | Name: |  |  |  |  |  |  |  |  |  |  |  | Range: | Unit: |  |  | Resol.: |  |  |  |
| 5.001 | DPT_Scaling |  |  |  |  |  |  |  |  |  |  |  | [0…100] | % |  |  | 0,4 % |  |  |  |
| 5.003 | DPT_Angle |  |  |  |  |  |  |  |  |  |  |  | [0…360] | ° |  |  | 1,4° |  |  |  |
| 5.004 | DPT_Percent_U8 |  |  |  |  |  |  |  |  |  |  |  | [0…255] | % |  |  | 1 % |  |  |  |

Examples

| Datapoint type | Encoded Value |  |  | Resolution |
| --- | --- | --- | --- | --- |
|  | 50 % | 100 % | 255 % |  |
| 5.001 | 80h | FFh | Out of encodable range. | 0,4 % |
| 5.004 | 32h | 64h | FFh | 1 % |

### Non-Scaled values

| Format: | 8 bit: U8 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| octet nr |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| field names |  | Unsigned Value |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Encoding |  | U | U | U | U | U | U | U | U |  |  |  |  |  |  |  |  |  |  |
| Encoding: | binary encoded |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Range: | UsignedValue = [0…255] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Datapoint types |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ID: | Name: |  |  |  |  |  |  |  |  |  |  |  | Range: |  | Unit: |  |  | Resol.: |  |
| 5.010 | DPT_Value_1_Ucount |  |  |  |  |  |  |  |  |  |  |  | [0…255] |  | counter pulses |  |  | 1 counter pulse |  |

## 8 Bit with Sign

### General

DPT 6.xxx is defined for transmitting values from -128 up to +127.

Negative numbers are represented as two’s complement. To do so, the binary representation of the positive number is inverted and 1 is added.

### Datapoint types V8 - Signed Relative Value

| Format: | 8 bit |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| octet nr |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| field names |  | RelSigned Value |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| encoding |  | V | V | V | V | V | V | V | V |  |  |  |  |  |  |  |  |  |  |
| Encoding: | Two's complement notation |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Range: | -128 … 127 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Datapoint types |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ID: | Name: |  |  |  |  |  |  |  |  |  | Range: |  |  |  | Unit: |  |  | Resolution |  |
| 6.001 | DPT_Percent_V8 |  |  |  |  |  |  |  |  |  | -128 % … 127 % |  |  |  | % |  |  | 1 % |  |
| 6.010 | DPT_Value_1_Count |  |  |  |  |  |  |  |  |  | -128 … 127 |  |  |  | counter pulses |  |  | 1 counter pulse |  |

## 2 Octet without Sign

### General

DPT 7.xxx is defined for transmitting values up to 65535.

### 2-octet unsigned counter value

| Format: |  | 2 octets: U16 |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| octet nr |  |  | 2 MSB |  | 1 LSB |  |  |  |  |  |  |  |  |
| field names |  |  | UnsignedValue |  |  |  |  |  |  |  |  |  |  |
| encoding |  |  | UUUUUUUU |  | UUUUUUUU |  |  |  |  |  |  |  |  |
| Encoding: |  | Binary encoded value |  |  |  |  |  |  |  |  |  |  |  |
| Range: |  | UnsignedValue = [0…65535] |  |  |  |  |  |  |  |  |  |  |  |
| Datapoint types |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ID: | Name: |  |  |  |  | Range: |  |  |  |  | Unit: |  | Resol.: |
| 7.001 | DPT_Value_2_Ucount |  |  |  |  | [0…65 535] |  |  |  |  | pulses |  | 1 pulse |

| Format: |  | 2 octets: U16 |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| octet nr |  |  | 2 MSB |  | 1 LSB |  |  |  |  |  |  |  |  |
| field names |  |  | TimePeriod |  |  |  |  |  |  |  |  |  |  |
| encoding |  |  | UUUUUUUU |  | UUUUUUUU |  |  |  |  |  |  |  |  |
| Encoding: |  | Binary encoded value |  |  |  |  |  |  |  |  |  |  |  |
| Range: |  | UnsignedValue = [0…65535] |  |  |  |  |  |  |  |  |  |  |  |
| Datapoint types |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ID: | Name: |  |  |  |  | Range: |  |  |  |  |  | Unit: | Resol.: |
| 7.002 | DPT_TimePeriodMsec |  |  |  |  | 0 ms … 65535 ms |  |  |  |  |  | ms | 1 ms |
| 7.003 | DPT_TimePeriod10Msec |  |  |  |  | 0 s … 655,35 s |  |  |  |  |  | ms | 10 ms |
| 7.004 | DPT_TimePeriod100Msec |  |  |  |  | 0 s … 6 553,5 s |  |  |  |  |  | ms | 100 ms |
| 7.005 | DPT_TimePeriodSec |  |  |  |  | 0 s … 65 535 s (≅ 18,2 hours) |  |  |  |  |  | S | 1 s |
| 7.006 | DPT_TimePeriodMin |  |  |  |  | 0 min … 65 535 min (≅ 45,5 days) |  |  |  |  |  | min | 1 min |
| 7.007 | DPT_TimePeriodHrs |  |  |  |  | 0h … 65 535 h (≅ 7,4 years) |  |  |  |  |  | h | 1 h |

## 2 Octet with Sign

### General

DPT 8.xxx is defined for transmitting values from -32768 up to +32767. As for 1 octet with sign, negative values are transferred as two’s complement.

### 2-octet signed counter value

| Format: |  | 2 octet: V16 |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| octet nr |  |  | 2 MSB |  | 1 LSB |  |  |  |  |  |  |  |  |
| field names |  |  | SignedValue |  |  |  |  |  |  |  |  |  |  |
| encoding |  |  | VVVVVVVV |  | VVVVVVVV |  |  |  |  |  |  |  |  |
| Encoding: |  | Two’s complement notation |  |  |  |  |  |  |  |  |  |  |  |
| Range: |  | SignedValue = [-32 768 … 32 768] |  |  |  |  |  |  |  |  |  |  |  |
| Datapoint types |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ID: | Name: |  |  |  |  | Range: |  |  |  |  | Unit: |  | Resol.: |
| 8.001 | DPT_Value_2_Count |  |  |  |  | [-32 768 … 32 767] a) |  |  |  |  | pulses |  | 1 pulse |
| 8.010 | DPT_Percent_V16 |  |  |  |  | -327,68 % ... 327,67 %b) |  |  |  |  | % |  | 0,01 % |
| a) Only for DPT_Value_2_Ucount, the value 7FFFh can be used to denote invalid data. b) For DPT_Percent_, the value 7FFFh shall be used to denote invalid data. |  |  |  |  |  |  |  |  |  |  |  |  |  |

## 2 Octet Floating Point Number

### General

DPT 9.xxx is defined for transmitting floating point values. Various Datapoint types have been defined for different physical variables.

Not all Datapoint types use the maximum value range. Devices shall ignore invalid or undefined values.

The value to be transferred shall be coded in the mantissa. If the value multiplied by 100 (because of the resolution of 0,01) does not fit in the range of –2048 and +2047, the mantissa shall be divided by a factor, which constitutes the exponent. The sign bit indicates whether the value is a negative (S bit = 1) or a positive value (S bit =0). In case of negative values, the mantissa shall moreover be the two’s complement of the corresponding positive value.

### Datapoint types 2-Octet Float Value

| Format: |  | 2 octets: F16 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| octet nr |  |  | 2 MSB |  |  |  |  |  |  |  |  | 1 LSB |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| field names |  |  | FloatValue |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| encoding |  |  | M | E | E | E | E | M | M | M | M | M | M | M | M | M | M | M | M |  |  |  |  |  |  |  |
| Encoding: |  | FloatValue = (0,01*M)*2(E) E = [0 … 15] M = [-2 048 … 2 047], two’s complement notation For all Datapoint types 9.xxx, the encoded value 7FFFh shall always be used to denote invalid data. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Range: |  | [-671 088,64 … 670 760,96] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Datapoint types |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ID: | Name: |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Range: |  |  |  |  |  |  |  | Unit: |  | Resol.: |
| 9.001 | DPT_Value_Temp |  |  |  |  |  |  |  |  |  |  |  |  |  |  | -273 °C … 670 760 °C |  |  |  |  |  |  |  | °C |  | 1 °C |
| 9.002 | DPT_Value_Tempd |  |  |  |  |  |  |  |  |  |  |  |  |  |  | -670 760 K … 670 760 K |  |  |  |  |  |  |  | K |  | 1 K |
| 9.003 | DPT_Value_Tempa |  |  |  |  |  |  |  |  |  |  |  |  |  |  | -670 760 K/h … 670 760 K/h |  |  |  |  |  |  |  | K/h |  | 1 K/h |
| 9.004 | DPT_Value_Lux |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0 Lux … 670 760 Lux |  |  |  |  |  |  |  | Lux |  | 1 Lux |
| 9.005 | DPT_Value_Wsp |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0 m/s … 670 760 m/s |  |  |  |  |  |  |  | m/s |  | 1 m/s |
| 9.006 | DPT_Value_Pres |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0 Pa … 670 760 Pa |  |  |  |  |  |  |  | Pa |  | 1 Pa |
| 9.007 | DPT_Value_Humidity |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0 % … 670 760 % |  |  |  |  |  |  |  | % |  | 1 % |
| 9.008 | DPT_Value_AirQuality |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0 ppm … 670 760 ppm |  |  |  |  |  |  |  | ppm |  | 1 ppm |
| 9.010 | DPT_Value_Time1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  | -670 760 s … 670 760 s |  |  |  |  |  |  |  | s |  | 1 s |
| 9.011 | DPT_Value_Time2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  | -670 760 ms … 670 760 ms |  |  |  |  |  |  |  | ms |  | 1 ms |
| 9.020 | DPT_Value_Volt |  |  |  |  |  |  |  |  |  |  |  |  |  |  | -670 760 mV… 670 760 mV |  |  |  |  |  |  |  | mV |  | 1 mV |
| 9.021 | DPT_Value_Curr |  |  |  |  |  |  |  |  |  |  |  |  |  |  | -670 760 mA … 670 760 mA |  |  |  |  |  |  |  | mA |  | 1 mA |
| 9.022 | DPT_PowerDensity |  |  |  |  |  |  |  |  |  |  |  |  |  |  | -670 760 W/m2 … 670 760 W/m2 |  |  |  |  |  |  |  | W/m2 |  | 1 W/m2 |
| 9.023 | DPT_KelvinPerPercent |  |  |  |  |  |  |  |  |  |  |  |  |  |  | -670 760 K/% … 670 760 K/% |  |  |  |  |  |  |  | K/% |  | 1 K/% |
| 9.024 | DPT_Power |  |  |  |  |  |  |  |  |  |  |  |  |  |  | -670 760 kW … 670 760 kW |  |  |  |  |  |  |  | kW |  | 1 kW |
| 9.025 | DPT_Value_Volume_Flow |  |  |  |  |  |  |  |  |  |  |  |  |  |  | -670 760 l/h … 670 760 l/h |  |  |  |  |  |  |  | l/h |  | 1 l/h |
| 9.026 | DPT_Rain_Amount |  |  |  |  |  |  |  |  |  |  |  |  |  |  | -670 088,64 l/m² … 670 760,96 l/m² |  |  |  |  |  |  |  | l/m² |  | 0,01 l/m² |
| 9.027 | DPT_Value_Temp_F |  |  |  |  |  |  |  |  |  |  |  |  |  |  | -459,6 °F to 670 760,96 °F |  |  |  |  |  |  |  | °F |  | 0,01 °F |
| 9.028 | DPT_Value_Wsp_kmh |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0 km/h … 670 760,96 km/h |  |  |  |  |  |  |  | km/h |  | 0,01 km/h |

### Example

A temperature value of - 30 degrees C can be calculated according DPT 9.001 as follows:

Step 1: Calculate the mantissa

Due to the resolution of 0.01, the value to be coded must be multiplied by 100:

30 x 100 = 3000

Step 2: Check if exponent is required

Mantissa is 11 bits, range is from + 2047 to -2048.

3000 is larger, therefore exponent is required.

Which exponent? 21 = 2 is sufficient as 3000 : 2 = 1500, and this number can be coded in the mantissa.

Step 3: Code the mantissa:

| Value: | 1024 | 512 | 256 | 128 | 64 | 32 | 16 | 8 | 4 | 2 | 1 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Number: | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 |

If the number is negative, then create a two’s complement!

Output value:	101 1101 1100

Invert:		010 0010 0011

+1		                      1

-------------------------------------------------

010 0010 0100

Step 4: Code sign and exponent

Number is negative, therefore the S bit = 1

Exponent = 1, coded in four bits = 0001

Step 5: Final result

-30 = 1   0001   010 0010 0100

## Time

### General

DPT 10.001 is defined for transmitting the time of the day (e.g. cyclically by a system clock).

### Datapoint type Time

| Format: |  | 3 octets: N3U5r2U6r2U6 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| octet nr. |  |  | 3 MSB |  |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  | 1 LSB |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| field names |  |  | Day |  |  | Hour |  |  |  |  |  | 0 | 0 | Minutes |  |  |  |  |  |  |  | 0 | 0 | Seconds |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Encoding |  |  | N | N | N | U | U | U | U | U |  | r | r | U | U | U | U |  | U | U |  | r | r | U | U | U | U | U | U |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Encoding: |  | binary encoded |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Datpoint Types |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ID: | Name: |  |  |  |  |  |  |  |  |  |  | Field: |  |  |  |  |  | Encoding: |  |  |  |  |  |  |  |  |  |  |  |  |  | Range: |  |  |  |  |  |  |  | Unit: |  |  |  |  |  |  | Resol.: |  |  |  |  |
| 10.001 | DPT_TimeOfDay |  |  |  |  |  |  |  |  |  |  | Day |  |  |  |  |  | 1 = Monday … 7 = Sunday 0 = no day |  |  |  |  |  |  |  |  |  |  |  |  |  | [0…7] |  |  |  |  |  |  |  | none |  |  |  |  |  |  | none |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | Hour |  |  |  |  |  | binary encoded |  |  |  |  |  |  |  |  |  |  |  |  |  | [0…23] |  |  |  |  |  |  |  | hours |  |  |  |  |  |  | h |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | Minutes |  |  |  |  |  | binary encoded |  |  |  |  |  |  |  |  |  |  |  |  |  | [0…59] |  |  |  |  |  |  |  | minutes |  |  |  |  |  |  | min |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | Seconds |  |  |  |  |  | binary encoded |  |  |  |  |  |  |  |  |  |  |  |  |  | [0…59] |  |  |  |  |  |  |  | seconds |  |  |  |  |  |  | s |  |  |  |  |

## Date

### General

DPT 11.001 is defined for transmitting the date of the day (e.g. cyclically by a system clock). Please note that the day of the week is not transmitted in DPT 11.001.

It shall be noted that values shall be interpreted as follows by a receiver:

Year data  90 signifies year in the 20th century.

Year data < 90 signifies year in the 21st (this) century.

The encoding therefore covers years between 1990 and 2089.

Example:

YYYYYYY = 99d equals 1999

YYYYYYY = 0d equals 2000

YYYYYYY = 4d equals 2004

### Datapoint type Date

| Format: | 3 octets: r3U5r4U4r1U7 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| octet nr. |  | 3 MSB |  |  |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  | 1 LSB |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| field names |  | 0 | 0 | 0 | Day |  |  |  |  |  |  | 0 | 0 | 0 | 0 | Month |  |  |  |  | 0 | Year |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Encoding |  | r | r | r | U | U | U | U |  | U |  | r | r | r | r | U | U | U | U |  | r | U | U | U | U | U |  | U | U |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Encoding: | All values binary encoded. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Datpoint Types |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ID: | Name: |  |  |  |  |  |  |  | Field: |  |  |  |  |  |  |  | Range: |  |  |  |  |  |  |  |  |  | Unit: |  |  |  |  |  |  |  |  |  |  |  | Resol.: |  |  |  |  |  |  |  |  |  |  |
| 11.001 | DPT_Date |  |  |  |  |  |  |  | Day |  |  |  |  |  |  |  | [1…31] |  |  |  |  |  |  |  |  |  | Day of month |  |  |  |  |  |  |  |  |  |  |  | 1 day |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | Month |  |  |  |  |  |  |  | [1…12] |  |  |  |  |  |  |  |  |  | Month |  |  |  |  |  |  |  |  |  |  |  | 1 month |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | Year |  |  |  |  |  |  |  | [0…99] |  |  |  |  |  |  |  |  |  | Year |  |  |  |  |  |  |  |  |  |  |  | 1 year |  |  |  |  |  |  |  |  |  |  |

## Date and Time

DPT 19.001 is defined for transmitting the date and time of the day.
The Datapoint type combines and extends the DPT_TimeOfDay (10.001) and DPT_Date (11.001) and has a size of 8 bytes.

In this Datapoint type, the year is encoded as an unsigned byte and calculated as an offset to the year 1900. The period between 1900 and 2155 is thus covered with this Datapoint type.

### Datapoint type Time and Date

| Format: |  | 8 octets: U8[r4U4][r3U5][U3U5][r2U6][r2U6]B16 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| octet nr. |  | 8 MSB |  |  |  |  |  |  |  |  |  |  | 7 |  |  |  |  |  |  |  |  | 6 |  |  |  |  |  |  |  |  |  | 5 |  |  |  |  |  |  |  |  |  |
| field names |  | Year |  |  |  |  |  |  |  |  |  |  | 0 | 0 | 0 | 0 | Month |  |  |  |  | 0 | 0 | 0 | DayOfMonth |  |  |  |  |  |  | DayOfWeek |  |  |  | HourOfDay |  |  |  |  |  |
| Encoding |  | U | U |  | U | U | U | U | U |  | U |  | r | r | r | r | U | U | U | U |  | r | r | r | U | U | U | U |  | U |  | U | U |  | U | U | U | U | U | U |  |
| octet nr. |  | 4 |  |  |  |  |  |  |  |  |  |  | 3 |  |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  | 1 LSB |  |  |  |  |  |  |  |  |  |
| field names |  | 0 | 0 |  | Minutes |  |  |  |  |  |  |  | 0 | 0 | Seconds |  |  |  |  |  |  | F | WD | NWD | NY | ND | NDoW | NT |  | SUTI |  | CLQ | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |
| Encoding |  | r | r |  | U | U | U | U | U |  | U |  | r | r | U | U | U | U | U | U |  | B | B | B | B | B | B | B |  | B |  | B | r |  | r | r | r | r | r | r |  |
| Datapoint types |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ID: | Name: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 19.001 | DPT_DateTime |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Field |  |  |  | Description |  |  |  |  |  | Encoding |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Range |  |  |  |  | Unit |  |  |  | Resol.: |  |  |  |
| Year |  |  |  | Year |  |  |  |  |  | Value binary encoded, offset 1900 0 = 1900 255 = 2155 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | [0…255] |  |  |  |  | year |  |  |  | 1 year |  |  |  |
| Month |  |  |  | Month |  |  |  |  |  | Value binary encoded 1 = January … 12 = December |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | [1…12] |  |  |  |  | Month |  |  |  | 1 month |  |  |  |
| DayOfMonth |  |  |  | D |  |  |  |  |  | Value binary encoded 1 = 1st day 31 = 31st day |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | [1…31] |  |  |  |  | none |  |  |  | none |  |  |  |
| DayOfWeek |  |  |  | Day of week |  |  |  |  |  | Value binary encoded 0 = any day 1 = Monday … 7 = Sunday |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | [0…7] |  |  |  |  | none |  |  |  | none |  |  |  |
| HourOfDay |  |  |  | Hour of day |  |  |  |  |  | Value binary encoded. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | [0…24] |  |  |  |  | h |  |  |  | 1 h |  |  |  |
| Minutes |  |  |  | Minutes |  |  |  |  |  | Value binary encoded. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | [0…59] |  |  |  |  | min |  |  |  | 1 min |  |  |  |
| Seconds |  |  |  | Seconds |  |  |  |  |  | Value binary encoded. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | [0…59] |  |  |  |  | s |  |  |  | 1 s |  |  |  |
| F |  |  |  | Fault |  |  |  |  |  | 0 = Normal (No fault) 1 = Fault |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | {0,1} |  |  |  |  | none |  |  |  | none |  |  |  |
| WD |  |  |  | Working Day |  |  |  |  |  | 0 = Bank day (No working day) 1 = Working day |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | {0,1} |  |  |  |  | none |  |  |  | none |  |  |  |
| NWD |  |  |  | No WD |  |  |  |  |  | 0 = WD field valid 1 = WD field not valid |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | {0,1} |  |  |  |  | none |  |  |  | none |  |  |  |
| NY |  |  |  | No Year |  |  |  |  |  | 0 = Year field valid 1 = Year field not valid |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | {0,1} |  |  |  |  | none |  |  |  | none |  |  |  |
| ND |  |  |  | No Date |  |  |  |  |  | 0 = Month and Day of Month fields valid 1 = Month and Day of Month fields not valid |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | {0,1} |  |  |  |  | none |  |  |  | none |  |  |  |
| NDOW |  |  |  | No Day of Week |  |  |  |  |  | 0 = Day of week field valid 1 = Day of week field not valid |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | {0,1} |  |  |  |  | none |  |  |  | none |  |  |  |
| NT |  |  |  | No Time |  |  |  |  |  | 0 = Hour of day, Minutes and Seconds fields valid 1 = Hour of day, Minutes and Seconds fields not valid |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | {0,1} |  |  |  |  | none |  |  |  | none |  |  |  |
| SUTI |  |  |  | Standard Summer Time |  |  |  |  |  | 0 = Time = UT+X 1 = Time = UT+X+1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | {0,1} |  |  |  |  | none |  |  |  | none |  |  |  |
| CLQ |  |  |  | Quality of Clock |  |  |  |  |  | 0 = clock without ext. sync signal 1 = clock with ext. sync signal |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | {0,1} |  |  |  |  | none |  |  |  | none |  |  |  |

### Comments

#### Year field

The year is encoded on 8 bits instead of on 7 bits as in DPT_Date.

#### Hour field

The encoding of the hour is within the range [0…24] instead of [0…23].

When the hour is set to "24", the values of octet 3 (Minutes) and 2 (Seconds) shall be set to zero. Messages with invalid values ("Hour = 24", Minutes and Seconds not zero) have to be ignored by the receiver. 
In this way, it is possible to use this Datapoint type to encode e.g. schedule programs. In daily schedule programs usually "end of day" is encoded as 24:00:00 and not 23:59:59; otherwise there would be a 1 s "break" at midnight.

Without the value 24:00:00 one can not differentiate between a full 24 h period and a 0 h period.

Examples:

A daily program with 24 h comfort level is encoded as "start comfort: 00:00:00" and "end of comfort: 24:00:00".

A daily program with 0 h comfort level ( all day economy level) is encoded as "start comfort: 00:00:00" and "end of comfort: 00:00:00".

#### Fault field

"Fault" is set if one or more supported fields of the Date & Time information are corrupted. This is not the same as when the NY, ND, NW etc. attributes would be set (in this case the corresponding fields are not supported).

"Fault" is set e.g.

After power-down, if battery backup of the clock was not sufficient

After 1st start-up of the device (clock unconfigured)

Radio-clock (DCF 77) had no reception for a very long time

"Fault" is usually cleared automatically by the device (producer) if the local clock is set or clock data is refreshed by other means (e.g. by reception of system clock message, reception of DCF 77 radio message etc.).

The receiver (e.g. the user interface of a room unit) will interpret Date & Time with "Fault" as corrupted and will either ignore the message or show --:--:-- or blinking 00:00:00 (as known from video recorders after power-up).

#### SUTI field

SUTI is only an attribute for information / visualisation. In the hour field, summer-time correction is already considered. Therefore no hour offset shall be added by the receiver if SUTI is set.

SUTI = 0 standard time

SUTI = 1 summer daylight saving time

#### NDoW field

NDoW = 1	means that the “Day of Week”-field ddd is invalid and the ddd information shall be ignored. A Clock not supporting Day of Week information shall set NdoW = 1.

NDoW = 0 and ddd = 0	means that the ddd-field is valid and that ddd is a wildcard. This encoding feature is thought for use in for instance scheduling information.

#### CLQ field

Bit 7 of the 1st byte is used for “Quality of Clock” bit (CLQ). The other bits of this byte are reserved for future extensions. Their values shall be 0. If this Datapoint typeDatapoint type is used for transmitting data, transmitters shall set the lower 7 bits to 0. Receivers shall check these bits to be 0.

Encoding

0:	Clock without an external synchronisation signal. 
The device sending date & time information has a local clock, which can however be inaccurate !

1:	Clock with an external synchronisation signal (like DCF77, videotext, etc.). 
The device sending date & time information sends signals which are synchronised (time to time) with external date & time information.

The default value is 0.

Also an externally synchronised clock should send CLQ = 0 after start-up (until reception of first synchronisation signal) or after a synchronisation timeout.

## 4 Octet without Sign

### General

DPT 12.xxx is defined for transmitting unsigned counter values up to 4294967295.

### Datapoint typeDatapoint types 4-Octet Unsigned Value

| Format: |  | 4 octets: U32 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| octet nr |  |  | 4 MSB |  |  |  |  |  |  |  |  | 3 |  |  |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  | 1 LSB |  |  |  |  |  |  |  |  |
| field names |  |  | UnsignedValue |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| encoding |  |  | U | U | U | U | U | U | U | U |  | U | U | U | U |  | U | U | U | U |  | U | U | U | U | U | U |  | U | U |  | U | U | U | U | U | U | U | U |  |
| Encoding: |  | Binary encoded |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Range: |  | UnsignedValue = [0…4 294 967 295] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| PDT |  | PDT_UNSIGNED_LONG |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Datapoint typeDatapoint types |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ID: | Name: |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Unit: |  |  |  |  |  |  |  |  |  |  |  | Resol.: |  |  |  |  |  |  |  |  |  |  |  |  |
| 12.001 | DPT_Value_4_Ucount |  |  |  |  |  |  |  |  |  |  |  |  |  |  | counter pulses |  |  |  |  |  |  |  |  |  |  |  | 1 pulse |  |  |  |  |  |  |  |  |  |  |  |  |

## 4 Octet with Sign

### General

DPT 13.xxx is defined for transmitting signed counter values from -2147483648 up to +2147483647, where negative values are transmitted as 2’s complement.

### Datapoint type 4-Octet Signed Value

| Format: |  | 4 octets: V32 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| octet nr |  |  | 4 MSB |  |  |  |  |  |  |  |  | 3 |  |  |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  | 1 LSB |  |  |  |  |  |  |  |  |  |  |
| field names |  |  | SignedValue |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| encoding |  |  | V | V | V | V | V | V | V | V |  | V | V | V | V |  | V | V | V | V |  | V | V | V | V | V | V | V | V |  | V | V | V | V | V | V | V | V |  |  |  |
| Encoding: |  | Two’s complement notation |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Range: |  | SignedValue = [-2 147 483 648 … 2 147 483 647] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| PDT |  | PDT_LONG |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Datapoint typeDatapoint types |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ID: | Name: |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Range: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Unit: |  | Resol.: |
| 13.001 | DPT_Value_4_Count |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | counter pulses |  | 1 pulse |

## 4 Octet Floating Point Number

### General

DPT 14.xxx is defined for floating point values with greater accuracy. Various Datapoint types have been defined depending on the different physical variables.

The IEEE floating point format is used in accordance with IEEE 754 so that

higher values than for DPT 9.xxx can be transferred,

compatibility to other systems using this format is ensured.

79 different Datapoint types have been defined, of which some are given in the underneath paragraph.

### Datapoint types 4-Octet Float Value

| Format: | 4 octets: F32 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| octet nr. |  | 4 MSB |  |  |  |  |  |  |  |  | 3 |  |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  | 1 LSB |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| field names |  | S | Exponent |  |  |  |  |  |  |  |  | Fraction |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| encoding |  | F | F | F | F | F | F | F | F |  | F | F | F | F | F | F | F | F |  | F | F | F | F | F | F | F | F |  | F | F | F | F | F | F | F | F |  |  |  |  |  |  |  |  |  |  |
| Encoding: | The values are encoded in the IEEE floating point format according IEEE 754. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Range: | S (Sign) = {0,1} Exponent = [0 … 255] Fraction = [0 … 8 388 607] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| Datpoint Types |  |  |  |  |
| --- | --- | --- | --- | --- |
| ID: | Name: | Unit: | Resol.: | Comment: |
| 14.007 | DPT_Value_AngleDeg | ° | 1 ° | angle, degree |
| 14.019 | DPT_Value_Electric_Current | A | 1 A | electric current |
| 14.027 | DPT_Value_Electric_Potential | V | 1 V | electric potential |
| 14.028 | DPT_Value_Electric_PotentialDifference | V | 1 V | electric potential difference |
| 14.031 | DPT_Value_Energy | J | 1 J | energy |
| 14.032 | DPT_Value_Force | N | 1 N | force |
| 14.033 | DPT_Value_Frequency | Hz = s-1 | 1 Hz | frequency |
| 14.036 | DPT_Value_Heat_FlowRate | W | 1 W | heat flow rate |
| 14.037 | DPT_Value_Heat_Quantity | J | 1 J | heat, quantity of |
| 14.038 | DPT_Value_Impedance |  | 1 | impedance |
| 14.039 | DPT_Value_Length | m | 1 m | length |
| 14.051 | DPT_Value_Mass | kg | 1 kg | mass |
| 14.056 | DPT_Value_Power | W | 1 W | power |
| 14.065 | DPT_Value_Speed | m s-1 | 1 m s-1 | speed |
| 14.066 | DPT_Value_Stress | Pa = N m-2 | 1 Pa | stress |
| 14.067 | DPT_Value_Surface_Tension | N m-1 | 1 N m-1 | surface tension |
| 14.068 | DPT_Value_Common_Temperature | °C | 1°C | temperature, common |
| 14.069 | DPT_Value_Absolute_Temperature | K | vK | temperature (absolute) |
| 14.070 | DPT_Value_TemperatureDifference | K | 1 K | temperature difference |
| 14.078 | DPT_Value_Weight | N | 1 N | weight |
| 14.079 | DPT_Value_Work | J | 1 J | work |

## Access Control

### General

DPT 15.000 is defined to represent or log access procedures.

### Datapoint type DPT_Access_Data

| Format: |  |  |  | 4 octets: U4U4U4U4U4U4B4N4 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| octet nr. |  |  |  | 4 MSB |  |  |  |  |  |  |  |  |  | 3 |  |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  | 1 LSB |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| field names |  |  |  | D6 |  |  |  |  | D5 |  |  |  |  | D4 |  |  |  | D3 |  |  |  |  | D2 |  |  |  | D1 |  |  |  |  | E |  | P | D | C | Index |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| encoding |  |  |  | U | U |  | U | U | U | U | U | U |  | U | U | U | U | U | U | U | U |  | U | U | U | U | U | U | U | U |  | b |  | b | b | b | N | N | N | N |  |  |  |  |  |  |  |  |  |  |  |
| Encoding: |  | D6, D5, D4, D3, D2, D1: binary encoded value N: binary encoded value E, P, D, C: See below |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Range: |  | See below. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Unit: |  | Not applicable. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Resol.: |  | Not applicable. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Datapoint types |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ID: |  |  | Name: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 15.000 |  |  | DPT_Access_Data |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Field |  |  |  |  | Description |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Encoding |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Range |  |
| D6, D5, D4, D3, D2, D1 |  |  |  |  | digit x (1…6) of access identification code. Only a card or key number should be used. System number, version number, country code, etc. are not necessary. Ciphered access information code should be possible in principle. If 24 bits are not necessary, the most significant positions shall be set to zero. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Values binary encoded. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | [0 … 9] |  |
| E |  |  |  |  | Detection error |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0 = no error 1 = reading of access information code was not successful). |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | {0,1} |  |
| P |  |  |  |  | Permission (informs about the access decision made by the controlling device) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0 = not accepted 1 = accepted |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | {0,1} |  |
| D |  |  |  |  | Read direction (e.g. of badge) If not used (e.g. electronic key) set to zero. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0 = left to right 1 = right to left |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | {0,1} |  |
| C |  |  |  |  | Encryption of access information. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0 = no 1 = yes |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | {0,1} |  |
| Index |  |  |  |  | Index of access identification code (future use) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Value binary encoded. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | [0 … 15] |  |

EXAMPLE 1	: Transmission of the access identification code “123456”, without error indication, permission accepted, badge read from left to right, no encryption and index 13.

| Octet 6 |  |  |  |  |  |  |  | Octet 7 |  |  |  |  |  |  |  | Octet 8 |  |  |  |  |  |  |  | Octet 9 |  |  |  |  |  |  |  | Octet 10 |  |  |  |  |  |  |  | Octet 11 |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 |
|  |  |  |  |  |  | APCI |  |  |  | r | r | r | r | r | r | D6 |  |  |  | D5 |  |  |  | D4 |  |  |  | D3 |  |  |  | D2 |  |  |  | D1 |  |  |  | E | P | D | C | Index |  |  |  |
|  |  |  |  |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 1 |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1 |  |  |  | 2 |  |  |  | 3 |  |  |  | 4 |  |  |  | 5 |  |  |  | 6 |  |  |  |  |  |  |  | 13 |  |  |  |

## Character String

### General

To transfer strings of characters, Datapoint types 16.000 and 16.001 allow sending text of up to 14 characters. The encoding of the individual characters corresponds to the Datapoint types 4.001 and 4.002. The contents in both cases starts with the MSB.

Two data types exist: DPT 16.001 (DPT_String_ASCII – unused characters are set to value 00h) and DPT 16.002 (DPT_String_8859_1).

### Example

“KNX is OK” is transmitted as:

| K | N | X |  | i | S |  | O | K |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 4B | 4E | 58 | 20 | 69 | 73 | 20 | 4F | 4B | 00 | 00 | 00 | 00 | 00 |

## Scene Control

### General

In KNX three different approaches exist for setting scenes

Setting the scene conditions via ETS parameters and calling the desired parameterized scene by using the DPT_Scene_AB (1.022) 1 bit Datapoint type. In this case, it is not possible that the user changes the scene.

Setting the scene conditions of the connected actuators and storing this scene as a scene number in the connected actuators by using the DPT_Scene_Control. With the same DPT, scenes can thus be set and called.

By using the DPT_SceneNumber: this DPT is identical to the DPT_Scene_Control, however it does not allow to store new scenes.

### Datapoint type Scene Number

| Format: |  | 1 octet: r2U6 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| octet nr. |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| field names |  | r | r | SceneNumber |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| encoding |  | 0 | 0 | U | U | U | U | U | U |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| PDT: | PDT_GENERIC_01 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Datapoint types |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ID: |  | Name: |  |  |  |  |  |  |  |  |  | Encoding: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Resol: |  |  |  |  |  |  |  |  |  |  | Range: |  |  |  |  |  |  |  |  |  |
| 17.001 |  | DPT_SceneNumber |  |  |  |  |  |  |  |  |  | SceneNumber |  |  |  | Value binary encoded |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  | [0 … 63] |  |  |  |  |  |  |  |  |  |

### Datapoint type DPT_SceneControl

| Format: | 1 octet: B1r1U6 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| octet nr. |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| field names |  | C | R | SceneNumber |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| encoding |  | B | r | U | U | U | U | U | U |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Unit: | Not applicable. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Resol.: | Not applicable. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Datpoint Types |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ID: | Name: |  |  |  |  |  |  |  |  |  |  |  |  | Encoding: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Range: |  |  |  |  |
| 18.001 | DPT_SceneControl |  |  |  |  |  |  |  |  |  |  |  |  | C |  |  |  |  |  | 0 = activate the scene corresponding to the field Scene Number 1 = learn the scene corresponding to the field Scene Number |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | [0, 1] |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | R |  |  |  |  |  | Reserved (0) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | {0} |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | SceneNumber |  |  |  |  |  | Scene number |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | [0 … 63] |  |  |  |  |

## Common HVAC Datapoint types

### General

In earlier developments, the operating mode of room thermostat was set by one bit Datapoint types.

Since some years, a general new DPT_HVACMode has been introduced, of which the use has become obligatory for new developments. The operating mode may be additionally set by single bit DPTs.

Next to this, a number of enumerations have been standardised for amongst others building occupancy and building mode. 
Room thermostats inform on their status with the standardised DPT_HVACContrMode.

## Datapoint types N8

| Format: |  | 1 octet: N8 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| octet nr. |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| field names |  | field1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| encoding |  | N | N | N | N | N | N | N | N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Encoding: | Encoding absolute value N = [0 … 255] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Unit: | none |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Resol.: | none |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| PDT: | PDT_ENUM8 (alt: PDT_UNSIGNED_CHAR) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Datapoint types |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ID: | Name: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Encoding: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Range: |  |  |  |  |  |  |
| 20.002 | DPT_BuildingMode |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0 = Building in use 1 = Building not used 2 = Building protection |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | [0 …3] |  |  |  |  |  |  |
| 20.003 | DPT_OccMode |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0 = occupied 1 = standby 2 = not occupied 3 …255 not used; reserved |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | [0 … 3] |  |  |  |  |  |  |
| 20.102 | DPT_HVACMode |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0 = Auto 1 = Comfort 2 = Standby 3 = Economy 4 = Building Protection 5 … 255 = reserved |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | [0 … 4] |  |  |  |  |  |  |
| 20.105 | DPT_HVACContrMode |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0 = Auto 1 = Heat 2 = Morning Warmup 3 = Cool 4 = Night Purge 5 = Precool 6 = Off 7 = Test 8 = Emergency Heat 9 = Fan only 10 = Free Cool 11 = Ice 12 = Maximum Heating Mode 13 = Economic Heat/Cool Mode 14 = Dehumidification 15 = Calibration Mode 16 = Emergency Cool Mode 17 = Emergency Steam Mode 18 … 19 = reserved 18 … 19 = reserved 20 = NoDem 21 … 255 = reserved |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | {[0 … 17], 20} |  |  |  |  |  |  |

# Combination of DPTs into devices

## General

For two very common device types, the combination of DPTs into devices has been standardized and is obligatory for certification.

These standards called ‘functional blocks’ are respectively the “Dimming actuator basic” and the “Sunblind Actuator basic”.

## Functional Block – Dimming Actuator Basic

### General

A dimming actuator shall per channel at least support three group objects complying to the underneath stated DPTs:

Switch, DPT 1.001

Relative dimming, DPT 3.007

Absolute dimming, DPT 5.001

- Any other group objects are optional.

### Dimming Actuator Basic – Status Diagram

The basic function of the dimming actuator is described in the following status diagram.

A dimming actuator can find itself in one of three states – depending on which telegram(s) it receives:

| State | Description |
| --- | --- |
| Off | Dimming actuator is switched off |
| On | Dimming actuator is switched on, at least the lowest possible brightness is set |
| Dimming | Dimmer controller is enabled, brightness is adjusted in the direction of the setpoint |

The change from one state to another is triggered by so-called “events”. Events include:

| Name | Meaning |
| --- | --- |
| OFF command | Switching object receives value 0 |
| ON command | Switching object receives value 1 |
| Dimming up | Dimming object receives a new value, upward dimming direction |
| Dimming down | Dimming object receives a new value, downward dimming direction |
| Stop | Dimming object receives value ‘Stop’ |
| Dimming value OFF | Brightness object receives value 0 |
| Dimming value x % | Brightness object receives value > 0 |
| Value reached | Brightness has reached setpoint |

The event “Value reached” is an internal event. The function of the application software of a dimming actuator is illustrated by the following status diagram. The ellipses represent the states while the arrows represent the events.

This behaviour is checked during KNX certification tests.

## Functional Block – Sunblind Actuator Basic

### General

The function “Drive Control” is used primarily for controlling blind and roller shutter motors.

A sunblind actuator shall per channel at least support two group objects complying to the underneath stated DPTs:

Step/Stop (DPT 1.007)

Up/Down (DPT 1.008)

Any other group objects are optional.

Important: Group objects using this function shall not reply to read requests through the bus (Group Value Read messages). This restriction ensures that drives are not inadvertently set into motion. The READ flag of the group objects shall therefore be reset! This applies both to sensors AND actuators!

If devices are not of the type BCU 1, the above is not needed, provided that the update flag in the respective group objects are not set.

### Sunblind Actuator Basic – Status Diagram

An actuator for the control of blinds and shutters may be in one of four states, depending on the type of telegram(s) received:

| Status | Description |
| --- | --- |
| Stopped | No movement |
| In motion | The connected drive moves upwards or downwards |
| Step UP | The drive is in the step mode and is moved upwards by one step |
| Step DOWN | The drive is in the step mode and is moved downwards by one step |

(Depending on the type of application, it is of course possible to declare other directions of movement than those stated above, e.g. right/left or forwards/backwards.
Example: motor-driven sliding door.)

The following events trigger the changeover from one status to another:

| Name | Meaning |
| --- | --- |
| Move UP | Move object receives value ‘0’ |
| Move DOWN | Move object receives value ‘1’ |
| Step UP | Step object receives value ‘0’ |
| Step DOWN | Step object receives value ‘1’ |
| Time elapsed | Time limit defined for the motion of one step or for the entire range of motions has run out. |

The event ‘Time elapsed’ is an internal event. The operation of an actuator for the control of blinds and shutters is illustrated by the following status diagram. The ellipses represent the states whereas the arrows indicate the events. This behaviour is checked during KNX certification tests.

OEM: Original Equipment Manufacturer