## Slide 1: KNX Advanced Course
Telegram

## Slide 2: Transmission of a telegram - general
Event (e.g. Push button is pressed)
   Bus device sends a telegram on the bus
Bus ≥ t1 not occupied
   Transmission starts
t2
  Checking whether the telegram has been received correctly by the addressed DVC
Acknowledgement
  All „addressed“ bus devices acknowledge the receipt of the telegram simultaneously
Duration of telegram: 20 to 40 ms
Telegram
Ack.
t1
t2
Previous
Ack.

## Slide 3: Structure of a telegram
KNX Telegram = Header + useful data
  Header = bus specific data
  Useful data = information of the event (e.g. pressing a push button in KNX).
Telegram consists of a sequence of characters
1st character
Control field
1 byte
Source address
2 byte
Destination address
2 byte + 1 bit
Routing counter 3 bit
Length
4 bit
Useful data
Up to 16 x 1 byte
Check byte
1 byte
2nd character
3rd character
…
…

## Slide 4: Telegram – Time requirement
Transmission speed = 9600 bit/s
One bit occupies the bus  1/9600 s = 104 µs
One character:
  1 Startbit ST
  1 Stoppbit SP
  1 Paritybit P
  8 bit Information D0 bis D7
  2 Bit Pausenzeit
  = 1,35 ms pro Zeichen
ST
D0
D1
D2
D3
D4
D5
D6
D7
P
SP
Pause
Transmission time character: 1,35 ms

## Slide 5: Telegram – Time requirement
Transmission time telegram: 20 to 40 ms
Telegram
Ack.
t1
t2
Depending on the useful data
  Length of the telegram: 8 to 23 characters
Acknowledgement
  1 character
t1 Bus free time
  50 bit
t2 Pause until acknowledgement
  13 bit
  =================================
Occupation of bus: 20 to 40 ms
Most common telegrams: 20 ms
Maximum number of telegrams per second: 50 or 25

## Slide 6: Telegramm - Acknowledgement
Telegram
Ack.
t1
t2
D 7 | D 6 | D 5 | D 4 | D 3 | D 2 | D 1 | D 0 | Reading direction of the data bits
1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | BUSY = Device unable to process new information
0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | NACK = Reception incorrect
1 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | ACK = Reception correct

## Slide 7: Telegram – Numbering systems
Numbering system | Decimal | Binary | Hexadecimal
Base | 10 | 2 | 16
Digits | 0, 1, 2…9 | 0,1 | 0, 1…9, A, B…F
Numbering system: Base + digit
  Largest digit = smaller than the base by 1
Numbering systems
  Decimal = Most common numbering system
  Binary
    Important for computing
    Two states of a memory location (0,1)
    Content memory location = bit
  Hexadecimal
    One location = 4 bits of the binary system
    Clearer representation of data

## Slide 8: Telegram – Data formats
Size of data | Representable values | Term in digital technology | KNX Application (selection)
1 bit | 2 | Bit | Switching
2 bit | 4 |  | Priority
4 bit | 16 | Tetrad, nibble | Dimming
8 bit | 256 | Byte | 8-bit value
16 bit | 65.536 | Word | Floating point
32 bit | 4.294.967.296 | Double word | Counter
Data format
  For processing data
  Representation of the contents of the data in binary, hexadecimal or decimal.

## Slide 9: Number conversions
Splitting into individual powers
Converting a binary or hexadecimal
number into a decimal number
Dividing procedure
Converting a decimal number into a
binary or hexadecimal number
Leserichtung
HEX  Decimal
  Splitting up into ist individual powers
  Adding up
Decimal  Binary
  Number is constantly divided by the base
  Until 0
  Remainder of the division = digits of the converted number
  Digits of the converted number = Reach from back to front

## Slide 10: Control field
D 7 | D 6 | D 5 | D 4 | D 3 | D 2 | D 1 | D 0 | Reading direction of the data bits
1 | 0 | R | 1 | P | P | 0 | 0 | PP = Transmission priority, R= Repetition, other bits fixed
 |  |  |  | 0 1 0 1 | 0 0 1 1 |  |  | System functions (highest priority) Alarm functions (alarm) High operational priority (normal) Low operational priority (auto)
 |  | 0 |  |  |  |  |  | Repeat
Control field
1 byte
Source address
2 byte
Target address
2 byte + 1 bit
Routing counter 3 bit
Length
4 bit
Useful data
Up to 16 x 1 byte
Check byte
1 byte

## Slide 11: Source address (individual address)
B
B
B
B
B
B
B
B
A
A
A
A
L
L
L
L
0…15
0…15
0…255
AREA
LINE
BUS DEVICE
Structure:
Possible values:
Source address
  Individual address of the sending bus device
Control field
1 byte
Source address
2 byte
Target address
2 byte + 1 bit
Routing counter 3 bit
Length
4 bit
Useful data
Up to 16 x 1 byte
Check byte
1 byte

## Slide 12: Target address (when group address)
S
S
S
S
S
S
S
S
Mi
Mi
Mi
0…31
0…7
0…255
3-level structure
M
M
M
M
M
0…31
0…2047
2-level structure
M
M
M
M
M
S
S
S
S
S
S
S
S
S
S
S
Control field
1 byte
Source address
2 byte
Target address
2 byte + 1 bit
Routing counter 3 bit
Length
4 bit
Useful data
Up to 16 x 1 byte
Check byte
1 byte
Target address
  Normally a group address
  Bit after target address defines the type of the target address
  Determines which devices shall react to the telegram
  With one group address one or more DVCs can be addressed at the same time
Classification in levels
  For a better visual representation in ETS
  Group addresses are always stored in binary format in devices
/
/
/

## Slide 13: Check byte
Control field
1 byte
Source address
2 byte
Target address
2 byte + 1 bit
Routing counter 3 bit
Length
4 bit
Useful data
Up to 16 x 1 byte
Check byte
1 byte
D0 – D7
  Data bits of the 8 bit blocks
S0 – S7
  Bits of the check byte block (odd parity)
P
  Parity bit across character (even parity)
=
=
+
+
D7
D6
D5
D4
D3
D2
D1
D0
P
0
D7
D6
D5
D4
D3
D2
D1
D0
P
D7
D6
D5
D4
D3
D2
D1
D0
P
0
S7
S6
S5
S4
S3
S2
S1
S0
P
0
= 1
+
= 1
+
+
+
=
=
0